## Panel 120_240
[5 empty] | PANEL: | SP1
VOLTAGE: | 120/240 |  |  |  | PANEL BUS: |  | AMPS |  |  |  | 200 AMP SERVICE PEDESTAL - CIRCUIT CAPACITY CALCULATION SCHEDULE
PHASE, WIRES: | 1Ø, 3W |  |  |  | MAIN BREAKER: | 200 | AMPS |  |  |  | SERVICE PEDESTAL NAME |  | SP1
SCCR (AMPS): | [10 empty] | SERVICE PEDESTAL STREET ADDRESS |  | 190 N MAIN ST
SOURCE: | [10 empty] | CONDITION, IF EXISTING PEDESTAL |  | N/A
NOTES
DESCRIPTION |  | LOAD (Watts) | Breaker Size (Amps) | Circuit # | A | B | Circuit # | Breaker Size (Amps) | LOAD (Watts) | DESCRIPTION | CIRCUIT NAME |  | CIRCUIT # 1 |  | CIRCUIT # 3 |  | CIRCUIT # 5/7 |  |  | CIRCUIT # 9 |  | CIRCUIT # 11 |  | CIRCUIT # 13 |  | CIRCUIT # 15 |  | CIRCUIT # 17 |  | CIRCUIT # 19 |  | CIRCUIT # 21 |  | CIRCUIT # 23 |  | CIRCUIT # 2/4 |  | CIRCUIT # 6/8 |  | CIRCUIT # 10 |  | CIRCUIT # 12 |  | CIRCUIT # 14 |  | CIRCUIT # 16 |  | CIRCUIT # 18 |  | CIRCUIT # 20 |  | CIRCUIT # 22 |  | CIRCUIT # 24
TRAFFIC SIGNAL CABINET |  | 4800 | 60 | 1 | 51.5 |  | 2 | 60 | 1380 | STREETLIGHT #1 | CIRCUIT TYPE |  | TRAFFIC SIGNAL CABINET |  | INTERSECTION LIGHTING |  | CLV TELECOM CABINET |  |  | SMALL CELL SITE #1 |  | SMALL CELL SITE #2 |  | SMALL CELL SITE #3 |  | SPARE |  | SPARE |  | BLANK COVER |  | BLANK COVER |  | BLANK COVER |  | STREETLIGHT #1 |  | STREETLIGHT #2 |  | PHOTOCELL CONTROL |  | POLE OUTLETS #1 |  | POLE OUTLETS #2 |  | POLE OUTLETS #3 |  | POLE OUTLETS #4 |  | BLANK COVER |  | BLANK COVER |  | BLANK COVER
INTERSECTION LIGHTING |  | 2004 | 40 | 3 |  | 28.2 | 4 |  | 1380
CLV TELECOM CABINET |  | 1920 | 20 | 5 | 27.5 |  | 6 | 60 | 1380 | STREETLIGHT #2 |  |  |  |  | CLV TELECOM |  | POLE OUTLETS #1 |  |  | POLE OUTLETS #3 |  | POLE OUTLETS #4 |  | Intersection Lighting |  | SPARE |  | SPARE | [7 empty] | STREETLIGHT #1 |  | STREETLIGHT #2
|  | 1920 |  | 7 |  | 27.5 | 8 |  | 1380
SMALL CELL SITE #1 |  | 0 | 20 | 9 | 1 |  | 10 | 20 | 120 | PHOTOCELL CONTROL | VOLTAGE |  | 120 |  | 120 |  | 120 | / | 240 | 120 |  | 120 |  | 120 |  | 120 |  | 120 |  | 120 |  | 120 |  | 120 |  | 240 |  | 240 |  | 120 |  | 120 |  | 120 |  | 120 |  | 120 |  | 120 |  | 120 |  | 120
SMALL CELL SITE #2 |  | 0 | 20 | 11 |  | 15 | 12 | 20 | 1800 | POLE OUTLETS #1 | CIRCUIT BREAKER CAPACITY (AMP) |  | 60 |  | 40 |  | 20 |  |  | 20 |  | 20 |  | 40 |  | 20 |  | 20 |  | 0 |  | 0 |  | 0 |  | 60 |  | 60 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20 |  | 20
SMALL CELL SITE #3 |  | 0 | 40 | 13 | 15 |  | 14 | 20 | 1800 | POLE OUTLETS #2 | MAXIMUM CURRENT DRAWN ALLOWED |  | 48 |  | 32 |  | 16 / Phase |  |  | 16 |  | 16 |  | 32 |  | 16 |  | 16 |  | 0 |  | 0 |  | 0 |  | 48 |  | 48 |  | 16 |  | 16 |  | 16 |  | 16 |  | 16 |  | 16 |  | 16 |  | 16
SPARE |  | 0 | 20 | 15 |  | 3 | 16 | 20 | 360 | POLE OUTLETS #3 | PHASE IDENTIFICATION |  | A |  | B |  | A & B |  |  | A |  | B |  | A |  | B |  | A |  | B |  | A |  | B |  | A & B |  | A & B |  | A |  | B |  | A |  | B |  | A |  | B |  | A |  | B
SPARE |  | 0 | 20 | 17 | 0 |  | 18 | 20 | 0 | POLE OUTLETS #4 | PROPOSED LOAD TYPES | WATTS PER LOAD TYPE | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS |  | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS | QTY. | AMPS
BLANK COVER |  | 0 | 0 | 19 |  | 0 | 20 | 20 | 0 | BLANK COVER
BLANK COVER |  | 0 | 0 | 21 | 0 |  | 22 | 20 | 0 | BLANK COVER | PHOTOCELL CIRCUIT | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLANK COVER |  | 0 | 0 | 23 |  | 0 | 24 | 20 | 0 | BLANK COVER | TRAFFIC SIGNAL CABINET | 4800 | 1 | 40 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | TOTALS | 95 | 73.7 | AMPS |  |  |  | CLV TELECOM CABINET – DUPLEX OUTLET #1 | 1920 | 0 | 0 | 0 | 0 | 1 | 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | CLV TELECOM CABINET – DUPLEX OUTLET #2 | 1920 | 0 | 0 | 0 | 0 | 1 | 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | LIGHTING CONTACTOR #1 = | 60 Amp, 2-Pole | [5 empty] | POLE GFCI DUPLEX OUTLET (10 MAX PER CIRCUIT) | 180 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 10 | 15 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | LIGHTING CONTACTOR #2 = | 60 Amp, 2-Pole | [5 empty] | LIGHT FIXTURE TYPE 1 - 100' ROW (STAGGERED) | 251 | 0 | 0 | 8 | 16.7 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 11.5 | 11 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | LIGHT FIXTURE TYPE 2 - N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | LIGHT FIXTURE TYPE 3 - N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LOAD CALCULATIONS: |  |  |  | SUBTOTAL (VA): | 20244 | [5 empty] | LIGHT FIXTURE TYPE 4 - N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | +25% PER NEC (VA): | 5061 | [5 empty] | LIGHT FIXTURE TYPE 5 - N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | TOTAL (VA): | 25305 | @ 240V, 1Ø = 105.5 AMPS |  |  |  |  | LIGHT FIXTURE TYPE 6 - N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NOTES: | [10 empty] | SMALL CELL SITE | 320 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1. STREETLIGHT CIRCUITS SHALL HAVE A FUSED DISCONNECT AT EACH LIGHT POLE TO PTOTECT THE FIXTURE AND WIRE WITHIN THE POLE. | [10 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. ALL SERVICE PANELS SHALL BE PROVIDED WITH THE BREAKERS AND BLANK COVERS AS SHOWN.
[11 empty] | TOTAL EXISTING LOAD AMPS (COORDINATE WITH TEFO) = |  | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[11 empty] | TOTAL PROPOSED NEW LOAD ON CIRCUIT (AMPS) = |  | 40 |  | 16.7 |  | 32 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 11.5 |  | 11.5 |  | 1 |  | 15 |  | 15 |  | 3 |  | 0 |  | 0 |  | 0 |  | 0
[11 empty] | TOTAL REMAINING AVAILABLE CIRCUIT LOAD AMPS = |  | 8 |  | 15.3 |  | 0 |  |  | 16 |  | 16 |  | 32 |  | 16 |  | 16 |  | 0 |  | 0 |  | 0 |  | 36.5 |  | 36.5 |  | 15 |  | 1 |  | 1 |  | 13 |  | 16 |  | 16 |  | 16 |  | 16
[11 empty] | TOTAL LOAD ON SERVICE PEDESTAL = |  |  |  |  | 145.7 |  | AMPS
[11 empty] | TOTAL LOAD AVAILABLE ON SERVICE PEDESTAL = |  |  |  |  | 160 |  | AMPS | [36 empty] | Bold Indicates Size of New Breaker
[11 empty] | TOTAL REMAINING AVAILABLE SERVICE PEDESTAL LOAD (AMPS) = |  |  |  |  | 14.3 |  | AMPS
<<< ------------------------ UNHIDE COLUMNS WHEN STARTING & HIDE UNUSED COLUMNS WHEN FINISHED ------------------------ >>>

## Estimated Demand
LOAD CLASSIFICATION | CONNECTED LOAD |  | DEMAND FACTOR | ESTIMATED DEMAND
LIGHTING | "=SUM(X)" | VA | 125% | #VALUE!
RECEPTACLE (UP TO 10KVA) |  | VA | 100% | 0 VA
GREATER THAN 10KVA |  | VA | 50% | 0 VA
OTHER |  | VA | 100% | 0 VA
PANEL TOTALS |  |  |  | #VALUE!
#VALUE!